**ADDENDUM NUMBER 5**

**Friday, July 31, 2015**

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

**PROJECT: 15 MEDICAL PARK FIRE ALARM**

UNIVERSITY OF SOUTH CAROLINA

STATE PROJECT NO. H27-6111

LEA PROJECT NO. USC-2014-06

**\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_**

This addendum forms a part of the Construction Documents and modifies the original Bidding Documents dated

06.22.2015 and associated addendums as noted below. Acknowledge receipt of this addendum in the space provided on the Bid Form. Failure to do so may subject Bidder to disqualification.

**GENERAL:**

G1 Provide custom programming of fire alarm system to shut down all building air handling units when a general alarm occurs and/or when a duct detector alarm occurs (duct detectors are required to initiate a supervisory alarm).

G2 The bid closing for this project has been postponed until Friday, August 7th at 2PM. The closing will be held at 743 Greene Street; Columbia Campus, Conference Room 057.

**DRAWINGS:**

D4 Addendum 3, Item D4: Delete Item D4 in its entirety and replace with the following:

Drawing E-3, Fire Main Room 020L: Delete one flow switch and associated monitor module. Provide one Low-Air Monitor Switch and one Air Pressure Alarm Switch for dry sprinkler portion of sprinkler riser system. Provide one monitor module for each switch.

D8 Addendum 3, Item D8: Delete Item D8 in its entirety and replace with the following:

Drawing E-4, Women’s Restroom 105: Delete Note 5 on drawing. Delete the two duct smoke detectors and associated test stations shown in room and adjacent air shaft.

D9 Addendum 3, Item D9: Delete Item D9 in its entirety and replace with the following:

Drawing E-5, Women’s Restroom 240: Delete Note 1 on drawing. Delete the two duct smoke detectors and associated test stations shown in room and adjacent air shaft.

D12 Addendum 3, Item D12: Delete Item D12 in its entirety and replace with the following:

Drawing E-6, Women’s Restroom 364: Delete Note 1 on drawing. Delete the two duct smoke detectors and associated test stations shown in room and adjacent air shaft.

**END OF ADDENDUM NUMBER 5**